Α.2. Medium Voltage Panel (inside kiosk - medium voltage compartment)

For the drafting of this technical description, the products of ABB have been taken into account as indicative and not as binding. The contractor can offer products of corresponding specifications and certifications. In this case the contractor shall proceed to adjust the study based on the technical manuals of the company he will choose. It is emphasized that for reasons of uniformity, correct mechanical assembly and proper operation, each panel shall bear elements of only one company and the protocols that it provides shall be fully observed. The use of materials from different companies in the same table will not be accepted. Every installation that concerns medium voltage points is obliged to follow the technical specifications of each manufacturer based on the requirements of the application.

Indicative Panel:

The panel contains ABB materials.

Standard UniSec Medium Voltage points (combiners) of ABB, fully expandable, made of galvanized metal gussets. The front doors as well as their front covers are painted with RAL 7035 type paint.

UniSec air-insulated switchgear”, LSC2A-PM class, in terms of continuous operating losses according to IEC 62271-200.

“Arc fault tested” in accordance with IEC 62271-200

- IAC AFLR arc proof version, to the front, to the back and to the side

Guaranteed reliability and continuity of operation.

The metal partitions between the busbars and the cable compartments help to increase safety and continuity of operation.

UniSec Medium Voltage Panels are designed and tested (type tested) according to the IEC 62271-200 standard, while they have high resistance to internal arc faults.

UniSec Medium Voltage Panels comply with the following international standards:

IEC 62271-1 for general applications

IEC/EN 62271-200 for the Panel

- LSC2A Category of losses due to continuous operation

- PM compartmentalization category (metal compartment)

EN 62271-102 for the Earthing device

IEC 62271-100 	for the Automatic Power Switches

IEC 60071-2 		for the coordination of insulation

IEC 60470 		for the Contactors

IEC 60265-1 	for the  Load Switches

IEC 60529 		for the protection classes

IEEE 693		seismic test certification of the panel.

ELECTRICAL FEATURES

Rated voltage							kV		24

Test voltage (50-60 Hz x 1 min) 					kV 		50

Impulse testing voltage						kV 		125

Rated frequency						Hz 		50-60

Rated  busbar current					A 		630

Rated equipment current:

- GSEC load switch (SF6)					A 		 630

Rated short circuit resistance				kA (3s)		16

Overload                                                                                                kA                      40

Internal arc resistance (IAC AFLR)			kA(1s) 	16

OPERATING CONDITIONS

− Storage temperature:					-5°C ... +70°C

Ambient temperature range:				-5°C ... +40°C

− Maximum relative humidity without condensation:                 	95%

− Minimum relative humidity without condensation:    		 5%

− Altitude:  							<1000 m above sea

level

DEGREE OF PROTECTION

The categories of the degree of protection of the panel comply with the IEC 60529 standard.

− IP 4X outer cover (IP3X front switch operation)

− IP 2X separation among compartments

− IP 3X mechanical operating equipment.

DESIGN

Each unit is made entirely using pre-galvanized sheet metal. And consists of several compartments, as described in the following paragraphs.

The busbars compartment extends to the entire length of the panel.

Each unit has holes for mounting on the floor and openings for the passage of cables.

Handling and visit are performed from the front. All operations of the combiner will be made only with the door closed.

All units are equipped with a door with an inspection window and mechanical locking, which allows it to be opened only under safe conditions. 
Access to the interior shall only occur if all electrical parts of the combiner are

off and connected to the earthing. When the door is open all electrical components are locked and can only change status when the door is safely closed.

With proper mechanical latches between door grounding-switches, the correct sequence of

operations and staff will be ensured.

It is also possible to lock the combiner doors with padlocks that all open with the

same key.

A plate with full verbal and diagrammatic instructions for operating the combiner is

placed on the front of the combiner to ensure its proper and safe operation.

Also, there are distinct signs of danger from the presence of medium voltage.

Metal lifting hoops are placed on the top of the combiner to facilitate its

movement. Each combiner can be transferred independently so that flexibility and scalability can be

achieved.

The combiners have suitable mechanical interconnection points and interconnection of the copper busbars (Cu) to connect with other combiners easily and safely.

COMPARTMENTALISATION

Each unit consists of several power compartments:

cable compartment [8], busbars compartment [4] and equipment compartment [5].

The compartments are metal-separated from each other by the load switch. The units may be equipped with an auxiliary circuit compartment [7], in which all the instruments and wiring are located.

AUXILIARY CIRCUIT - EQUIPMENT COMPARTMENT

It is at the top of the point and includes the low-voltage materials required for

operation and control (relays, buttons, switches, etc.)  as well as any other auxiliary equipment, meeting paragraphs 5.4 of IEC 62271-200 and 5.4 of IEC 60694.

To facilitate identification of the control circuits, the cables are marked at both ends. The minimum cross section of the wires will be:

- 2,5 mm for power circuits

-       1  mm   for the rest

The compartment is accessible even if the point is under voltage.

BAR SYSTEM

The busbars compartment contains the main busbar system which is connected to the fixed upper contacts of the load switch. The main busbars are made of "full radius edge” electrolytic copper of 99.9% purity with PVC insulation.

Specifically:

1x30x10 mm for 630 A

GROUNDING BARS

The x3 mm ground busbar is made of radius edge electrolytic copper of 99.9% purity and extends along the panel while a flexible earth conductor is placed on the door.

SWITCH-DISCONNECTOR

The equipment is housed in a cover made of two materials:

the upper part is made of closed-type resin, to ensure the level of insulation and the lower part is made of stainless steel to ensure the metal separation and grounding between the busbars and cables compartments.

This metal separation (PM class according to IEC 62271-200) guarantees maximum safety (LSC2A class) for the staff in case of intervention in the cable compartment to replace the fuses or to check the cables, even with the busbars charged.

EARTHING SWITCH

Each incoming/outgoing unit may be equipped with an earthing switch for grounding the cables.

The same device can be used to ground the busbar system. It can also be installed directly on the central busbar system in a special cabin (busbar application).

The earthing switch has a short-circuit making capacity (except for the unit with fuses).

It is operated from the front of the panel while its position can be determined from the front of the panel via a mechanical indicator.

DETAILED DESCRIPTION OF MEDIUM VOLTAGE POINTS

The panel is composed of the following points (combiners)

  - one (1) P.P.C. arrival point    		SDC

  - one (1) measurement point (CURRENT TRANSFORMERS)    UMP

  - one (1) measurement point (VOLTAGE TRANSFORMERS)    SFV

  - two (2) measurement points (TRANSFORMERS)    SBC

Indicative panel dimensions: 2000x 1210 x 3179 mm (H x D x L).

SDC UniSec Type INPUT FIELD (combiner)

  - SDC P.P.C. Arrival point

indicative dimensions: 1700 x 1210x 375mm (H x D x L).

This includes:

| # DESCRIPTION |  |  |  | # COMPANY |  | # PCS |  |
| --- | --- | --- | --- | --- | --- | --- | --- |
| # SF6 LOAD SWITCH |  | # G-Sec/T2 |  | # ABB |  | # 1 |  |
| ## Three-pole Load Switch with double spring mechanism of sulfur hexafluoride (SF6), three (3) positions (line-open-earth) 24kV 630A 16kA (3sec) 50kV 125kVp with mimic diagram and earthing device. ## Auxiliary switch contacts 4+4 NO/NC for indicating the status of the switch and earthing device. ## Manual operating mechanism for the load switch and the earthing device. ## Switch working coil. ## Security lock -keys on the switch. ## Security lock -keys on the earthing device. |  |  |  |  |  |  |  |
| ## LINE LIGHTNING ROD |  | ## PBP |  | ## ABB |  | ## 3 |  |
| ## 10kA-line, 21kV indoor lightning rods ## Surge arresters with metal oxide resistors without spark gaps (MO surge arresters), direct molded silicone housing, designed and tested according to IEC 60099-4. |  |  |  |  |  |  |  |
| ## INDICATOR LIGHT SET |  | ## VPIS |  | ## ABB |  | ## 1 |  |
| ## Voltage indicator set with three (3) built-in lamps ## Set of three (3) capacitive distributors. |  |  |  |  |  |  |  |
| ## HEATING RESISTANCE |  |  |  | ## ΑΒΒ |  | ## 1 |  |
| ## 50W, 230V heating resistance, controlled by the respective thermostat |  |  |  |  |  |  |  |
| ## LOW VOLTAGE COMPARTMENT-EQUIPMENT BOX |  |  |  |  |  | ## 1 |  |
| ## Miniature circuit breakers, terminals, etc. for the smooth operation of the equipment |  |  |  |  |  |  |  |

UMP MEASUREMENT POINT (CURRENT TRANSFORMERS)

  - UMP Measurement Point (Current Transformers)

Indicative dimensions: 1700 x 1220x 750mm (H x D x L)

| # DESCRIPTION | # TYPE | # COMPANY | # PCS |
| --- | --- | --- | --- |
| ## DIN type current transformer…/5/5 | ## TPU 60.13 | ## ABB | ## 3 |
| ## 24kV indoor transformer made of epoxy resin with double winding in the secondary / 5 for measurement, 15VA class 1 and / 5 for protection, 10VA class 5P10 and with integrated capacitative distributors i.e. output for voltage indication (voltage indicator) |  |  |  |
| ## INDICATOR LIGHT SET | ## VPIS | ## ABB | ## 1 |
| ## Voltage indicator set with three (3) built-in lamps |  |  |  |
| ## HEATING RESISTANCE |  | ## ABB | ## 1 |
| ## 50W, 230V heating resistance, controlled by the respective thermostat |  |  |  |
| ## LOW VOLTAGE COMPARTMENT-EQUIPMENT BOX |  |  | ## 1 |
| ## Miniature circuit breakers, terminals, etc. for the smooth operation of the equipment |  |  |  |

MEASUREMENT POINT (Voltage transformer) 	SFV  UniSecType

  - SFV Measurement Point (Voltage Transformer)

Indicative dimensions: 1700 x 1220x 500mm (H x D x L)

| # DESCRIPTION | # TYPE | # COMPANY | # PCS |
| --- | --- | --- | --- |
| ## SF6 LOAD SWITCH | ## G-Sec/T2F | ## ABB | ## 1 |
| Three-pole, three-position (line-open-earth) sulfur hexafluoride Sulfur Load Switch, with double spring mechanism, 24kV 630A 16kA (3sec) 50kV 125kVp with mimic diagram, earthing, melting stop mechanism even for one (1) fuse and fuse bases. Manual operating mechanism for the load switch and the earthing device Mechanical indicator of melted fuse Security lock -keys on the switch Security lock -keys on the earthing device |  |  |  |
| ## FUSE 24kV/6A | ## CEF 24-6 | ## ABB | ## 3 |
| ## Medium Voltage fuses, rated current 6A and rated voltage 24 kV |  |  |  |
| ## DIN TYPE VOLTAGE TRANSFORMER | ## TJC6 | ## ABB | ## 3 |
| ## Single-pole voltage transformers made of epoxy indoor resin 50VA, class 0.5, 20,000: √3 / 100: √3 - 100: 3 V. The open triangle is closed with an adjustment-damping resistor for protection against magnetic resonance overvoltages |  |  |  |
| ## MODBUS RTU DIGITAL MULTI-INSTRUMENT | ## M4M 30 Modbus` | ## ABB | ## 1 |
| Electrical measuring instrument, ABB, M2M type that measures per line and three-phase VL-L, VL-N, A, Hz, W, Var, VA, kWh, kVarh, kVAh, cosφ, calculates current and voltage THD harmonic values, balance between consumed/produced power and energy and CO2 equivalent, maximum, minimum and average values of all electrically measured parameters. With 2 digital programmable contacts as pulse outputs for telemetry or alarm. |  |  |  |

| ## LOW VOLTAGE COMPARTMENT-EQUIPMENT BOX |  |  | ## 1 |
| --- | --- | --- | --- |
| ## Miniature circuit breakers, terminals, etc. for the smooth operation of the equipment |  |  |  |

TRANSFORMER PROTECTION POINTS UniSecType SBC (2 pcs)

  - SBC protection point

Indicative dimensions: 2000 (including low voltage box) x 1220x 750mm (H x D x L)

| # DESCRIPTION | # TYPE | # COMPANY | # PCS |
| --- | --- | --- | --- |
| ## SF6 LOAD SWITCH | ## G-Sec/IB | ## ABB | ## 1 |
| Three-pole sulfur hexafluoride (SF6) three (3)-position (line-open-earth) switch, with single spring mechanism, with mechanically latched ground lock, 24kV 630A 16kA (3sec) 50kV 125kVp with mimic diagram and security keys (works with SF6 HD4 / R-Sec circuit breaker) Cable earthing 24kV 16kA (3sec) 50kV 125kVp (full making capacity 62.5kAp) mechanically latched with the Load Switch and the combiner door Auxiliary switch contacts 4+4 NO/NC for indicating the status of the switch and earthing device Security lock -keys on the switch Security lock -keys on the earthing device |  |  |  |

| ## SF6 AUTOMATIC POWER SWITCH | ## HD4/R-Sec 24.06.12 | ## ABB | ## 1 |
| --- | --- | --- | --- |
| ## Automatic power switch made of sulfur hexafluoride (SF6), 24kV 630A 12.5kA (3sec) 50kV 125kVp with Closing Button, Opening Button, Mechanical indications of Switch (opening / closing), Mechanical indications of the spring (charged / discharged), Operations Meter, Safety off lock, Working Coil (YO1). |  |  |  |
| ## PROTECTION & CONTROL RELAY ## (inside wide low voltage box) | ## REF601 | ## ABB | ## 1 |
| ## External electronic relay with modbus port RTU RS485 for secondary overvoltage (I>), short circuit (I >>), leakage to ground protection, IEEE No: 51, 50/51, 50N / 51N ETC for cooperation with DIN type current transformer Analog inputs: 3 sensor and ground CT Binary I/O option: 4BI + 6 BO Power supply: 24-240 Vac/Vdc ## ===== Included: Voltage adapter AC/D |  |  |  |

| ## CURRENT SENSOR | ## KECA250B1 | ## ABB | ## 3 |
| --- | --- | --- | --- |
| ## 250A cl 05/5P125 |  |  |  |
| ## TOROIDAL TRANSFORMER | ## Τ110/P | ## ABB | ## 1 |
| ## Toroidal Φ110 transformer (cooperates with the relay) for earth leakage protection 50 / 1A, 1VA, class 3 |  |  |  |
| ## INDICATOR LIGHT SET | ## VPIS | ## ABB | ## 1 |
| ## Voltage indicator set with three (3) built-in lamps |  |  |  |
| ## HEATING RESISTANCE |  | ## ABB | ## 1 |
| ## 50W, 230V heating resistance, controlled by the respective thermostat |  |  |  |
| ## LOW VOLTAGE COMPARTMENT-EQUIPMENT BOX |  |  | ## 1 |
| ## Miniature circuit breakers, terminals, etc. for the smooth operation of the equipment |  |  |  |

level

DEGREE OF PROTECTION

The categories of the degree of protection of the panel comply with the IEC 60529 standard.

− IP 4X outer cover (IP3X front switch operation)

− IP 2X separation among compartments

− IP 3X mechanical operating equipment.

UNINTERRUPTIBLE POWER SUPPLY (UPS) SYSTEM

The power supply for all relays of the medium voltage switchboard will be done via an uninterruptible power supply (UPS) system, of 1.5 KVA and 60 minutes of autonomy.

TESTS

1.   Type tests

The Contractor shall be able to provide all TYPE Certificates of a corresponding series of 20KV switchboards (i.e. for Input Field, Current Transformers Field, Measurement and Output Fields) by recognized laboratories in Greece or abroad, at least for the following tests:

- impulse dielectric tests

- power frequency dielectric tests

- temperature-rise tests

- short-time withstand current tests

2.   Routine tests

The routine tests will be performed by the supplier of the MV switchboard and he will be obliged to provide a relevant certificate stating that at least the following tests, as defined in IEC 62271- 200, have been performed.

- power frequency dielectric tests

- dielectric tests on auxiliary and control circuits

- verification of the correct wiring

- mechanical operation tests.

Drafting of DEDDIE dossier for Substation Νο 1Β.

The dossier shall include all necessary designs and documents required by DEDDIE, even if not mentioned in this technical description, for the approval of the operation of Substation No 1Β of ThPA SA, following the installation and connection of the new 20KV switchboard of Substation No 1Β to the 20 KV combiner of DEDDIE and the new transformers.

The Contractor shall undertake all necessary procedures for disconnection and reconnection of the electricity of Substation 1Β of ThPA SA with DEDDIE, following consultation with the Authority.

- TECHNICAL DESCRIPTION FOR THE 2 DRY-TYPE 630 KVA TRANSFORMERS & THE STABLE BALANCE PANEL OF THE NEW TRANSFORMERS

- CORRECTION OF THE FLOOR PLAN, THE SINGLE-LINE DIAGRAM AND THE PRICE LIST, RESPECTIVELY